## Table 1
Typical Film Heat Transfer Coefficients for Shell-and-Tube Heat Exchangers
| Fluid Condition | W/m2-K
Sensible Heat Transfer
Water | Liquid | 5,000-7,500
Ammonia | Liquid | 6,000-8,000
Light organics | Liquid | 1,500-2,000
Medium Organics | Liquid | 750-1,500
Heavy Organics | Liquid
| Heating | 250-750
| Cooling | 150-400
Very heavy organics | Liquid
| Heating | 100-300
| Cooling | 60-150
Gas | 1-2 bar abs | 80-125
Gas | 10 bar abs | 250-400
Gas | 100 bar abs | 500-800
Condensing Heat Transfer
Steam, ammonia | No noncondensable | 8,000-12,000
Light Organics | Pure component, 01 bar abs, no noncondesnable | 2,000-5,000
Light Organics | 01 bar, 4% noncondensable | 750-1,000
Medium Organics | Pure or narrow condensing range, 1 bar abs | 1,500-4,000
Heavy Organics | Narrow condensing range, 1bar abs | 600-2,000
Light multicomponent mixture, all condensable | Medium condensing range, 1bar abs | 1,000-2,500
Medium multicomponent mixture, all condensable | Medium condensing range, 1bar abs | 600-1,500
Heavy multicomponent mixture, all condensable | Medium condensing range, 1bar abs | 300-600
Vaporizing Heat Transfer
Water | Pressure < 5 bar abs, T = 25 K | 5,000-10,000
Water | Pressure 5-100 bar abs, T = 20 K | 4,000-15,000
Ammonia | Pressure < 30 bar abs, T = 20 K | 3,000-5,000
Light organics | Pure component, pressure < 30 bar abs, T = 20 K | 2,000-4,000
Light Organics | Narrow boiling range, pressure 20-150 bar abs, T = 15- 20 K | 750-3,000
Medium Organics | Narrow boiling range, pressure < 20 bar abs, T = 15 K | 600-2,500
Heavy Organics | Narrow boiling range, pressure < 20 bar abs, T = 15 K | 400-1,500